## Slide 1: Phoenix Input/Output Controller

## Slide 2: Bus Controller
IL ETH BK DI8 DO4 2TX-PAC – PN 2703981
Notes: The controller comes with Ethernet communications, 4 digital outputs and 8 digital inputs. The outputs can be used for driving relays or low power alarm lights. The inputs could be used for door switches or vacuum pump monitoring, etc.

## Slide 3
Overview- Environmental hardware field architecture
5/22/2019
3

## Slide 5: Features
Provides power to individual modules
Integrated 4 digital outputs
Integrated 8 digital inputs
Stack 13 additional modules to expand the system
Mix digital and analog inputs and outputs with one controller
Ethernet communications to all sensors and outputs
Compact form factor

## Slide 6: Features
2 or 3 wire sensor technology on the same module
4-20mA, 0-20mA, 0-10V, etc all on the same module
16 bit resolution
Short circuit proof for passive sensor supply voltage, however, use fused terminal blocks for field wiring.
Diagnostic indicator LED’s
Worldwide availability with technical support

## Slide 7: Features
Color coded modules for ease of identification
  Black = power
  Pink = digital output
  Blue = digital input
  Green = analog input
DIN rail mount provide for grounding, both physical earth ground and functional earth ground
Eliminates parallel wiring of multiple modules

## Slide 8: PHOENIX CONTACT
www.phoenixcontact.com

## Slide 9: Specifications
General Data | 
Housing dimensions (width x height x depth) | 48.8 mm x 120 mm x 71.5 mm
Ambient temperature (operation) | -25°C to +55°C
Permissible humidity (operation) | 10% to 95%, according to DIN EN 61131-2
Connection data for Inline connector | 
Connection method | Spring-cage terminals
Conductor cross section | 0.2 mm2 to 1.5 mm2 (solid or stranded), 24 - 16 AWG
Transmission speed | 500kbps
Power consumption | 
Voltage | 24 VDC
Current | 52 mA

## Slide 10: Controller Wiring
24VDC +
24VDC +
24VDC +
24VDC -
24VDC -
Notes: The 24VDC power CAN be jumpered, but the preferred method is to power each terminal from a separate terminal block.

## Slide 12: Digital Output Module 4 or 32DO
Additional Modules:
IB IL 24 DO 4-PAC – 2861276
IB IL 24 DO 32HD-PAC - 2862822
Notes: It is possible to use digital outputs to control alarm lights or audio alarms or possibly to control power, through relays, to conveyors or other equipment.

## Slide 13: Digital Output Specifications
General Data | 
Housing dimensions (width x height x depth) | 12.2 mm x 140 mm x 71.5 mm
Ambient temperature (operation) | -25°C to +55°C
Permissible humidity (operation) | 10% to 95%, according to DIN EN 61131-2
Number of outputs | 4
Output voltage | 24 VDC
Maximum output current per channel | 500 mA
Protective circuit | Overload protection, short-circuit protection of outputs Zener diode in output chip

## Slide 14: Digital Output Wiring Slot 3-1,2,3,4
Slot 3-1
Slot 3-2
Slot 3-3
Slot 3-4

## Slide 16: Digital Input Module
Input 1, Slot 2-1
Input 2, Slot 2-2
Input 3, Slot 2-3
Input 4, Slot 2-4
Input 5, Slot 2-5
Input 6, Slot 2-6
Input 7, Slot 2-7
Input 8, Slot 2-8
Additional Module:
IB IL 24 DI 32HD-PAC - 2862835

## Slide 18: Analog Input Module
Additional Modules:
IB IL AI 2SF-PAC – 2861302
IB IL AI 8SF-PAC - 2861412

## Slide 19: Analog Input Wiring Slot 4-2
24VDC
Power Supply

## Slide 20: Analog Input Specifications
General Data | 
Housing dimensions (width x height x depth) | 12.2 mm x 120 mm x 71.5 mm
Ambient temperature (operation) | -25°C to +55°C
Permissible humidity (operation) | 10% to 95%, according to DIN EN 61131-2
Process data update of both channels | <1,5 ms
Behavior upon sensor failure | Goes to 0 mA/4 mA

## Slide 22: Slot Identification
Power Module-No slot number
Black Color
Digital Output—Alarms, etc
Pink Color
Slot 0-1
Slot 0-2
Slot 0-3
Slot 0-4

## Slide 23: Slot Identification
Digital Input—Door Switches,
Lt Blue Color
Slot 1-1
Slot 1-2
Slot 1-3
Slot 1-4
Slot 1-5
Slot 1-6
Slot 1-7
Slot 1-8

## Slide 24: Slot Identification
Digital Output—Alarms, etc
Pink Color
Slot 2-1
Slot 2-2
Slot 2-3
Slot 2-4
Digital Output—Alarms, etc
Pink Color
Slot 3-1
Slot 3-2
Slot 3-3
Slot 3-4

## Slide 25: Slot Identification
Analog Input, T/RH, Δ P, etc
Green Color
2 Inputs, up to 8
Slot 4-1
Slot 542

## Slide 26: Slot Identification
Analog Input, T/RH, Δ P, etc
Green Color
2 Inputs, up to 8
Slot 5-1
Slot 5-2
Analog Input, T/RH, Δ P, etc
Green Color
2 Inputs, up to 8
Slot 6-1
Slot 762
Can keep adding Modules up to 13

## Slide 27
IP adress Assign Tool

## Slide 34
Integrated webpage

## Slide 51: Questions??